Terms of Reference

to perform work

Major inspection of power unit No. 7

Labor safety risk level: high.

The risk level is determined in accordance with the standard STO No.UBP-S.17 “Contractors and business partners work management”

1. Branch Name.

Surgutskaya GRES-2 Branch Unipro PJSC.

2. Full name of the equipment (system), work site.

Surgutskaya GRES-2 Branch Unipro PJSC, 23 Energostroiteley str., bldg. 34, Surgut, Khanty-Mansiysk Autonomous District - Yugra, Tyumen Region, 628406.

Gas turbine unit 7 - sug_09000042.

Steam turbine unit 7 - sug_09000044.

Turbo generator unit 7 - sug_09000040.

Lubrication system Main building of power unit No. 7 - sug_09000089.

Control system Main building of power unit No. 7 - sug_10004338.

3. Grounds to perform work.

Approved repair program for 2025.

4. Purpose of the work.

4.1. Ensure long-term trouble-free operation of the Equipment.

4.2. Prevent damage to the Equipment.

4.3. Achieve maximum operation readiness of the Equipment.

5. Scope of Work.

5.1. Major inspection of power unit No. 7 as part of the following equipment manufactured by General Electric (hereinafter referred to as the Equipment):

- Gas turbine plant type 9FA – 1 pc;

- Gas fuel Skid – 1 pc;

- Lube oil skid – 1 pc;

- Hydraulic oil skid – 1 pc;

- D10 type steam turbine unit – 1 pc;

- Generator type 390H, including complete stator re-wedging – 1 pc.

Detailed scope of work for each unit of the Equipment, as well as the battery limit between the Contractor and the Owner are provided in Appendices 1a, 1b, 1c, 1d to these Terms of Reference.

  - The contractor, as part of the procurement documentation, shall provide a set of cost estimates for the cost of work under the offer prepared on the basis of the calculation in the form of Appendix No. 2 to the Terms of Reference with the mandatory indication of the following information:

- the cost of a man/hour and the labor intensity of the direct performer must be explained in detail by a justified calculation of the cost of a man/hour and a justified calculation of the labor intensity of the work to be carried out; The cost of a man/hour shall not exceed the amount given in the official data of the Unified Interdepartmental Statistical Information System of the Russian Federal State Statistics Service on the average payable monthly nominal wages of employees.

To justify the excess cost, an impersonal certificate of income and tax amounts of an actual performer of the work, signed by the Chief Accountant and the General Director for each position separately, shall be provided;

  - Thecost estimate documentation must include all expenses planned by the Contractor, including materials, machinery, transportation, procurement and storage, and travel expenses (if any).

  - Final payments for travel expenses shall be made by the Owner against actual documented expenses of the Contractor, based on the documents confirming such expenses, but not in excess of the amount included in the estimate documentation, which is an annex to the Contract. The Owner does not undertake any obligations to provide housing for the Contractor’s seconded personnel.

The following shall not be included in the travel expenses for reimbursement by the Owner and are not subject to compensation (including, but not limited to): services for: selection of housing, cleaning, laundry, food, and other expenses that are not directly lodging expenses.

The fact of lodging and staying in a rented accommodation of the Contractor’s employees in the city of Surgut during the period of performance of work under the Contract shall be confirmed by the Contractor provided the following: (1) a residential tenancy agreement (the text of the tenancy agreement shall provide the details of the Contractor’s employee: Full name, passport details with attached copies of documents confirming the Landlord’s ownership) and documents confirming the Contractor’s payment under the tenancy agreement, (2) documents (including payment documents) confirming the accommodation of the Contractor’s employees in the hotel (stating the employee’s details: full name and passport details).

Travel expenses to the place of business trip (city of Surgut) and back to the place of permanent work (including payments for issuing travel documents, expenses for using bedding on trains) shall be reimbursed to the Contractor in the amount of actual expenses substantiated by travel documents, but not to exceed the cost of travel:

- by rail

- in a compartment carriage of a high-speed branded train;

- by air in the economy class cabin;

- by road in a public transport vehicle (except taxis);

- any expenses associated with the use of personal transport during the mobilization of personnel, as well as when traveling to and from the place of work, shall not be reimbursed.

Copies of the reporting (supporting) documents stated above must be properly issued (bearing signatures of authorized persons and seal).

  - The costs of private health insurance shall not be reimbursed to the Contractor.

  - To clarify the scope of work under this TOR, the participant may send a request for clarification.

  - The Owner shall have the right to supplement, change, or exclude the scope of work specified in the Terms of Reference, based on the actual state of the facility when concluding the contract.

  - Estimate documentation must be submitted electronically in Excel format (.xls or .xlsx).

6. Requirements for the Contractor.

6.1. Mandatory Requirements:

6.1.1. The Contractor mast have necessary licenses and permits:

Individuals and companies authorized to perform the Work must have professional training in the following areas:

- major repairs of high-power combined-cycle gas turbines (400 MW +) manufactured by General Electric, Siemens, Ansaldo, etc. in a single-shaft arrangement with rigid shafts coupling of a gas turbine plant, steam turbine plant, and hydrogen-cooled generator;

- setting up combustion modes of gas turbine units manufactured by General Electric (combustion chamber DLN 2.6+) or similar;

- vibration adjustment and balancing of high-power single-shaft combined-cycle gas turbines (400 MW +) with rigid shaft coupling of a gas turbine plant, a steam turbine plant, and a generator, and having work experience with the Bentley Nevada vibration monitoring system.

6.1.2. The Contractor shall have the necessary technical and technological documentation from the General Electric manufacturer required to perform a major inspection of the power unit. The Owner does not have any documentation from General Electric manufacturer required to perform a major inspection of the power unit, and does not transfer it to the Contractor as part of fulfilling their contractual obligations.

6.1.3. The Contractor must have experience in performing similar works in terms of nature and scope at power engineering facilities or similar equipment for at least 3 years (experience in major repairs, vibration adjustment, and combustion mode setting of single-shaft combined cycle gas turbines manufactured by General Electric, Siemens, Ansaldo, etc. with a capacity of 400 MW or more).

6.1.4. The Contractor shall have a sufficient headcount of qualified personnel to perform all work as per the Terms of Reference, namely:

- Chief engineer for a gas turbine unit (at least 2 people to allow 2-shift work schedule on the Equipment) – minimum qualification: work at height;

- Chief Engineer for a steam turbine plant (at least 2 people to allow 2-shift work schedule on the Equipment) – minimum qualification: work at height;

- Chief Engineer for a generator (at least 2 people to allow 2-shift work schedule on the Equipment) – minimum qualification: work at height;

- Supervisor for a gas turbine unit (at least 2 people to allow 2-shift work schedule on the Equipment) – minimum qualification: work at height;

- Supervisor for a steam turbine unit (at least 2 people to allow 2-shift work schedule on the Equipment) – minimum qualification: work at height;

- Supervisor for a generator (at least 2 people to allow 2-shift work schedule on the Equipment) – minimum qualification: work at height;

- Gas turbine blade repair/installation specialist (at least 1 person) – minimum qualifications: work at height; work with electric, pneumatic, and abrasive tools;

- Generator stator wedging specialist (at least 4 people to allow 2-shift work schedule on the Equipment) - minimum qualifications: work at height; work with electric, pneumatic, and abrasive tools;

- Mechanic (5-6 category) (at least 40 people to allow 2-shift work schedule on each unit of the Equipment) – minimum qualifications: work at height; work with electric, pneumatic, and abrasive tools; hot work;

- Welder (at least 2 people to allow 2-shift work schedule on the Equipment) - minimum qualifications: work at height; work with electric, pneumatic, and abrasive tools; hot work;

- Rigger (at least 8 people to allow 2-shift work schedule on each unit of the Equipment) - minimum qualifications: handling operations; slinging work, work with hoisting equipment;

- Sandblasting specialist (at least 2 people to be able to make a separate team) – minimum qualifications: work at height; work with electric, pneumatic, and abrasive tools;

- Vibration adjustment and balancing specialist (at least 2 people to allow 2-shift work schedule on the Equipment);

- Combustion chamber mode setting specialist DLN 2.6+ (at least 2 people to allow 2-shift work schedule on the Equipment);

- Should the work be carried out by non-residents of the Russian Federation, the Contractor shall provide an interpreter at the work site to perform oral/written translation from the language of the Contractor’s representative into Russian (at least 2 people to allow 2-shift work schedule on the Equipment);

- Toolmaker (at least 2 people to allow 2-shift work schedule on the Equipment).

6.1.5. The persons provided by the Contractor and authorized to perform the work must have professional training confirmed by certificates for the right to perform the work, including:

- work at height (in accordance with the requirements of the Rules for labor safety when working at height, approved by Order No. 782n of the Ministry of Labor and Social Protection of the Russian Federation dated November 16, 2020);

- in electrical installations (personnel performing work in electrical installations and using power tools must have an electrical safety group relevant to the nature of the work performed and have a certificate of the established form in accordance with the requirements of the “Rules for labor protection during the operation of electrical installations”, approved by Order No. 903n of the Ministry of Labor of Russia on December 15, 2020);

- hot work;

- welding work;

- handling operations;

- slinging work, work with hoisting equipment;

- work with electric, pneumatic, and abrasive tools.

The Contractor’s personnel shall be subject to a knowledge test of the rules, regulations and instructions governing the performance of work and quality control in the manner established by the Federal Service for Environmental, Technological and Nuclear Supervision (Rostekhnadzor) of the Russian Federation, and shall have valid certification protocols in the field of industrial safety for carrying out certain types of work at hazardous production facilities (A1; B.1.11; B.8.3; B.9.3).

6.1.6. The Contractor must comply with the mandatory requirements in the field of occupational safety specified in Annex 3 to these Terms of Reference.

6.1.7. The Contractor must have the necessary equipment, labour saving devices, electric and pneumatic tools, devices, etc., required to perform the Work, such as:

- inch and metric metalworking tools (impact wrenches, open-end wrenches, heads, ratchets, taps, thread-cutting dies, drill bits, pullers, etc.);

- measuring and diagnostic tools/equipment (micrometers, protractors, calipers, hart communicators, multimeters, measuring clamps, etc.);

- induction heaters for steam turbine studs;

- dedicated hydraulic wrenches such as Avanti, HYTORC or similar, hydraulic jacks, hydraulic stud tensioners ITH, Riwerhawk;

- pneumatic equipment/tools and accessories (pneumatic tools, pneumatic hoses, pneumatic distribution systems, etc.);

- power tools;

- welding equipment;

- mobile sharpening machines;

- hoisting equipment and devices (hoists, slings, eye bolts, etc.), both Imperial and metric versions;

- Olympus IPLEX NX video endoscope or equivalent;

(the specified tools and equipment must be packed in an equipped tool holder with tools indexes to ensure their prompt issue and available stock in case of failure of the main set);

with the exception of stationary hoisting devices installed at the Owner’s repair sites, as well as tools and equipment provided by the Owner to perform the work in accordance with Annex 4 to these Terms of Reference.

6.1.8. The Contractor shall perform work using own resources or outsourcing the third parties (subcontractor) subject to a written approval by the Owner only. In the event of involving subcontracting companies, the Contractor shall be obliged to provide documents of such outsourcing providers in the scope applicable to the main Contractor at the stage of the procurement procedure.

6.2. Optional Requirements:

6.2.1. The Contractor shall have a quality management system in place that meets the requirements of ISO 9001:2011 Standard or ISO 9001:2015 (to be confirmed with the certificate).

6.2.2. The Contractor shall have positive references for performance of similar Works over the past three years for fuel and energy complex facilities.

6.2.3. The Contractor must comply with the optional requirements in the field of occupational safety specified in Annex 3 to the Terms of Reference.

6.2.4. Before submitting a technical and commercial proposal, it is advisable for the Contractor to arrive at the station for a preliminary inspection of the facility and the place where the work will be performed, to clarify the work conditions and to resolve any issues that may arise.

6.2.5. Positive work experience and absence of negative work experience over the past 3 years at the facilities of Unipro PJSC (breaches of contractual terms and conditions). The following indicators will be taken into account when assessing the participants’ proposals:

- Quality of products/services;

- Timely delivery/timely provision (availability) of services;

- Professional qualities of personnel (competence, abilities, experience, and flexibility);

- Compliance with safety requirements.

7. Requirements for performance of works

7.1. The Contractor shall perform the work in compliance with the occupational safety requirements specified in Annex 3 to these Terms of Reference.

7.2. The Contractor shall perform the work in compliance with STO No. SNPEB-R.07 (Union of Industrial and Environmental Safety Specialists) “Environmental Protection Rules for Contracting Organizations and Lessees of Unipro PJSC”.

7.3. While carrying out the work, the Contractor shall be guided by, observe, and comply with the requirements of the following regulatory and technical documents (signing the Contract shall mean that the Contractor has all of the following documents available during the work performance period):

- Terms of Reference;

- technical and process documentation, process charts, technological processes, manufacturer’s instructions, repair forms, drawings of the manufacturer General Electric for the performance of major inspection work;

- work performance project (hereinafter referred to as WPP). The Contractor shall develop a work performance plan in accordance with DD 153-34.0-20.608-2003 “Methodological guidelines, work performance plan for repair of power equipment of power plants, requirements for scope, content and design” and submit it to the Owner for approval 30 calendar days before the start of work). Work at Height Plan prepared and agreed upon with the Owner in accordance with the “Occupational Safety Rules for Working at Height” issued by Order No. 782n of the Ministry of Labor of Russia dated 16.11.2020 must be an integral part of the WPP.

7.4. Prior to the commencement of the Works (at least 30 calendar days prior to the commencement of the Works), the Contractor shall:

- determine the teams staff in terms of headcount, qualifications, and trades in accordance with the scope of repair. In which case, full employment of workers must be ensured during the work schedule time periods;

- appoint a manager to run the repair work (to execute the technical part of the contract) depending on the scope of work;

- appoint persons in charge of occupational safety, logistical support and compliance with the requirements of sanitary, epidemiological, and environmental legislation;

- develop and submit to the Owner for approval a detailed calendar (flowchart/timeline) schedule of work.

7.5. The measuring instruments used by the Contractor when performing the work must comply with the requirements of GOST R 8.674-2009 “State system for ensuring unity of measurements. General requirements for measuring instruments and technical systems and devices with measuring functions”, approved and put into effect by Order No. 1105-st of Rostekhregulirovanie dated 15.12.2009.

7.6. The measuring instruments used in performing repair work must be entered into the Federal Information Fund for ensuring unity of measurements, established in pursuance of Federal Law No. 102-FZ of 26.06.2008 “On ensuring unity of measurements”, and must have a valid passport and a certificate of verification or calibration.

7.7. The Contractor shall perform work through environmentally friendly ways that do not damage the quality of atmospheric air, water bodies, soils, and do not pollute the territory, production areas, and welfare buildings of the Owner.

7.8. When taking introductory occupational safety training course on the Owner’s territory, the Contractor’s personnel must produce knowledge testing certificates with a mark, certified by a seal, that they are fit to perform the work based on the results of a medical examination.

7.9. The scaffolding used by the Contractor to perform the work must be of knock-down type. The installation of scaffolding by the Contractor, the procedure for accepting it into operation, and the quality of the scaffolding must comply with the requirements of STO No. OTiBP-P.22 “Scaffolding management procedure in the branches of Unipro PJSC.”

7.10. The use of the scaffolding other than the knock-down type by the Contractor shall be permitted by way of exception, in which case, installation thereof must be carried out according to an individual project based on the calculations of the strength of all main elements, and the stability of the scaffolding in general. The project must be endorsed by the responsible person of the Contractor and approved by the chief engineer of the contracting organization, and then agreed upon with the head of the Occupational and Industrial Safety Service and the chief engineer of the branch.

8. Requirements for the provided materials and spare parts.

8.1. The Works within the scope of the Terms of Reference shall be performed using spare parts and materials provided by the Owner. The list of spare parts and materials provided by the Owner is specified in Annex 5a, b to these Terms of Reference.

9. Work performance deadlines

9.1. Work performance deadlines are as follows:

Work commencement date: October 01, 2025;

Work completion date: December 30, 2025;

9.2. At the stage of the procurement procedure, the Contractor shall provide in their proposal a milestones schedule for the Work performance. The commencement and completion dates of the work must not extend beyond the dates specified in Clause 9.1 of the ToR.

At the request of the Owner, the Contractor shall draw up a detailed schedule for the carrying out certain stages of work.

10. Requirements for acceptance of work.

10.1. Acceptance shall be carried out after all work has been completed.

10.2. The work shall be delivered based on the actual scope of work performed by means of inspection measurements, inspection of all work and signing of the Final Delivery and Acceptance Certificate for the work performed together with the handover of technical documentation for the work performed. Full acceptance shall be carried out in any case, regardless whether individual stages of the work have been accepted.

10.3. The work must be delivered in accordance with the work schedule and pursuant the “Regulations for the acceptance of work and equipment in terms of quality and quantity during repair, technical upgrading, and reconstruction work” STO No. URiTP-R-4.0.”

10.4. Types of tests:

- power unit idle operation to perform vibration adjustment;

- starting the power unit up to the nominal load to adjust the combustion mode within the entire adjustment range limits;

- integrated acceptance tests lasting 48 hours to confirm the loading/load shedding rates, minimum safe output, maximum available load, technical and economic performance indicators of the power unit (according to the indicators specified in Annex No. 6 to these Terms of Reference.

All start-ups/shutdowns of the equipment for the test purposes and the very tests shall be carried out by the Owner under the direct supervision of the Contractor at the work site. All tests shall be carried out according to the programs developed by the Contractor and agreed upon and approved by the Owner. Test programs must be approved not later than 30 calendar days before the test date.

11. Documentation to be submitted to the Owner.

11.1. List of entities involved in the production of works, names of engineering and technical personnel responsible for the performance of such work.

11.2. Statement of completed repair work (Annex 25 of the Maintenance and Repair Rules).

11.3. Delivery and acceptance certificate for the completed work.

11.4. Equipment fault detection reports (Annexes 22, 23 of the Maintenance and Repair Rules).

11.5. Technical acceptance certificate for repairs;

11.6. Certificate of recycled materials condition (if used);

11.7. Certificates of intermediate acceptance of certain units and structures.

11.8. Reports and protocols of equipment, circuits, and systems testing results.

11.9. Equipment acceptance certificates after individual testing and integral trial operation.

11.10. List of additional works not included in the standard scope of works for major repairs of the Equipment. The total scope and cost of additional work may not exceed the limit of such work established by the terms of the contract. The list of certain additional work and the timeframes for their completion must be agreed upon by the Owner before the work is actually started by the Contractor.

11.11. As-built documentation in accordance with DD 11-02-2006 “Requirements for the scope and procedure for keeping as-built documentation”.

11.12. Repair log books for repaired equipment.

11.13. WPP developed during performance of works.

11.14. Timesheets.

11.15. Other documentation the approved list of which shall sent by the Owner to the Contractor before the commencement of the work.

12. Contractor’s Guarantee:

The Contractor shall guarantee the following:

12.1. Proper quality of the Works in full in accordance with these Terms of Reference and current regulatory and technical documentation in force.

12.2.	Completion of all works within the deadlines.

12.3. Indemnification to the Owner for the damages caused by the defects revealed during the warranty period.

12.4. The Contractor shall be liable to the Owner for the damage caused by their acts or omissions to the Owner’s equipment and buildings in the amount of repair expenses.

12.5 The warranty period for the completed Work shall be 12 months from the date of signing the Final Delivery and Acceptance Certificate for the completed Work or from the date of transfer of the result of the completed Work under the Contract from the Contractor to the Owner (third party specified by the Owner) in the event of refusal to perform the Contract (termination of the Contract).

12.6. The Contractor guarantees that as a result of the work performed the guaranteed performance indicators of the Equipment set forth in Annex 6 to these Terms of Reference, determined based on the results of integral trial operation, will be achieved. All start-ups/shutdowns of the equipment for the test purposes and the very tests shall be carried out by the Owner under the direct supervision of the Contractor at the work site. All tests shall be carried out according to the programs developed by the Contractor and agreed upon and approved by the Owner. Test programs must be approved not later than 30 calendar days before the test date.

Annexes:

Annex 1a. Typical scope of major inspection of gas turbines.

Annex 1b. Typical scope of major inspection of steam turbines.

Annex 1c. Typical scope of major inspection of generators.

Annex 1d. Scope of work for generators beyond the standard ones.

Annex 2. Type of cost statement.

Annex 3. Occupational safety requirements.

Annex 4. Tools and equipment to be provided by the Owner.

Annex 5a. List of major spare parts to be provided by the Owner.

Annex 5b. List of consumable spare parts to be provided by the Owner.

Annex 5c. List of materials and spare parts for generator re-wedging to be provided by the Owner.

Annex 6. List of guaranteed performance indicators of the Equipment.